•  2227 South Street  •  P.O. Box 044170

•  Racine, Wisconsin 53404-7003

•  Phone:  262-681-1300  •  Fax:  262-681-1318

www.Marlo-Inc.com

# DETAILED EQUIPMENT SPECIFICATION

# MRG SERIES WATER SOFTENERS

## 1.0	SCOPE

  - Provide as indicated a factory assembled vertical pressure type water softener system shipped with manifold piping attached to the resin tank for ease of installation and start up.  The system shall be of an approved design as fabricated by a manufacturer regularly engaged in the production of water treatment equipment.  All equipment and material shall be supplied in compliance with the specifications as intended for a complete and operational system.

1.2	Qualified manufacturers of water treatment equipment of the type specified are Marlo Incorporated of Racine, Wisconsin (www.marlo-inc.com, 262-681-1300) or engineer’s approval equal.

2.0        GENERAL DESCRIPTION

2.1	The system, in compliance with equipment specifications, is described as an automatic (single) (alternating twin) (parallel twin) (parallel triple) water softener system meeting the performance and design data requirements as hereinafter specified.

2.2	The system specifications are based on Marlo Model MRG-                                              .

3.0	PERFORMANCE & DESIGN DATA

  - INFLUENT WATER ANALYSIS

Total Hardness	GPG as CaCO3

Iron (Fe)	ppm

Turbidity (NTU)

pH

3.2	EFFLUENT WATER QUALITY	ZERO GPG Hardness

(ASTM Soap Test Method)

3.3	DESIGN PARAMETERS

Continuous System Flow & Pressure Drop	_____ GPM @        psi

Peak System Flow & Pressure Drop	_____ GPM @        psi

Daily Water Usage	_____ Gallons/Day

Daily Hours of Water Demand	_____ Hours/Day

Operating Temperature Range	_____ F Maximum

Operating Pressure Range (System)	_____ PSIG

Electrical Requirements	      V      Hz

## 3.3	EQUIPMENT SCHEDULE

Softener Tanks		Qty.              Dia.                 in. Side Shell            in.

Service Valves		Size        in.       Type                      .

Softening Resin  	Qty.              cu. ft.

Brine Maker 		Qty.              Dia.                 in. Height            in.

Salt Storage		               lbs.

Regeneration Type	(Time clock) (Metered)

Water Meter (s)	Qty _______ Size _________ in. Type ___________.

## EQUIPMENT

## Resin Tank

## Softener resin tank(s) shall be constructed of composite fiberglass reinforced plastic (FRP) construction. The inner shell shall be constructed of high density polyethylene with an outer shell of continuous fiberglass roving. The maximum operating pressure shall be 150 psig and despised with a safety factor of 4:1 for minimum burst pressure. Maximum design temperature shall be rated for 120° F.  All tank service connections shall be integrally molded flanged openings. The pressure vessel support base shall be a tri-pod design and constructed of polyethylene. A minimum freeboard of 50% shall be provided for backwash expansion above the normal ion exchange resin bed level.

4.2	Tank Option

Provide pressure vessel stamped and certified in accordance with ASME Section X.  Maximum working pressure to be 150 psig and designed with a safety factor of 6:1 for minimum burst pressure.

4.3      	Upper Inlet Distributor

The upper distribution system shall be a single point baffle constructed of Schedule-80 PVC pipe and fittings.

4.4	Lower Outlet Distributor

The lower distributor system shall be of the hub and radial type design, constructed of PVC

with slotted full flow non-clogging replaceable ABS strainers and covered with a subfill of 1/8” x 1/16” washed gravel.

4.5	Main Operating Valves

The main operating valves shall be a nest of individual diaphragm valves.  The valves shall have Noryl thermoplastic bodies, Buna-N diaphragm and stainless steel and brass internal parts.  The valves shall be slow opening and closing, and free of water hammer.  There shall be no contact of dissimilar metals within the valves and no special tools shall be required to services the valves.  Valves can be operated either hydraulically or pneumatically. Basics of Design: Aquamatic K53 Series.

4.6	Brine System

The brine system shall be platform type with a dry salt storage compartment and a saturated brine compartment sufficient for at least four regenerations at full salting.  The tank shall be of polyethylene construction.  It shall be equipped with a float operated plastic brine valve and allow for simple adjustment of salt dosage without removal of salt or salt shelf system.  Provide an external automatic self-adjusting brine injector to draw brine and rinse at a constant rate regardless of water pressure in the range 30 to 100 PSI.  Brine injector shall be made of PVC and be sized to provide adequate brine draw for the specified softener system.

4.7        Softening Resin

Resin shall be of a premium grade high capacity, cation type, to be furnished in the sodium form.  It shall be stable over the entire pH range, have good resistance to bead fracture, and be insoluble in all common solvents.  The resin shall be capable of 30,000 grains per cubic foot capacity when regenerated with 15 lbs. NaCI.

4.8	Flow Control

An automatic backwash control shall be provided to maintain a proper backwash and fast flush flows over wide variations of operating pressure.  Controller shall contain no moving parts, and require no field adjustment.

4.9	Piping and Fittings

The main operating valves and manifold piping shall be factory assembled and shipped attached to the resin tank for ease of installation and start-up. Piping and fittings shall be Schedule 80 PVC.

4.10	Control System

A NEMA 4-X rated, factory mounted and wired electrical enclosure with all timing and sequencing controls for the softener shall be manufactured and provided by the same vendor providing the water treatment hardware.  The controls shall include an automatic regeneration timer having the capability of providing site adjustable regeneration steps of backwash, brine injection, brine displacement, flush and return to service.  Indicator lights on the controller shall display the current status of the system.  Basis of Design:  Marlo MX-II Electronic Controller.

A multi-ported pilot control stager shall be factory wired and pre-tubed to automatically pressure activate the main operating valves through the steps of regeneration.  An indicator on the stager indicates the cycle of operation at all times.  Complete function and control of all regeneration steps can be performed manually in the event of a power failure.

4.11	Skid Mounted / Pre-Piped / Pre-Wired Package

The softener resin tanks shall be skid mounted on a 4” channel iron skid (7.25 lbs. per foot, ASTM grade A-36).  The skid shall be cross-braced with 4” channel or angle iron.  All steel surfaces shall be finish coated with Safety Blue epoxy paint system. All interconnecting piping shall be Sch 80 PVC.

This shall include inlet and outlet PVC isolation ball valves for each tank and a PVC system bypass valve.  I	nlet, outlet and drain headers shall be provided and terminated at the skid edge.  All piping shall be suitably supported by channel supports anchored to the skid.  Electric wiring, where applicable, shall be complete between all inter unit controls and require only a single power source connection.

The inter unit wiring shall be contained in waterproof conduit.  All inter-tank hydraulic or pneumatic tubing shall be installed as part of the skid package.

The resin tanks are to be bolted to the skid.  Permanent attachment, or welding, will not be acceptable.  The entire skid mounted system shall be leak and electrically tested as a unit by the manufacturer before shipment.

The entire skidded system shall be factory hydrotested at 100 psig for a minimum of 2 hours. A complete hydrotest report shall be provided in the service manual.

- REGENERATION INITIATION OPTIONS (Choose One)

5.1      	Time Clock (Single Tank)

The 12-Day electrical time clock controller shall be fully adjustable to initiate regeneration at any hour of the day and any day of the week.

5.2      	Automatic Water Meter (Single Tank)

The single water softener shall be equipped with one (1) turbine or paddle-type water meter in the outlet piping.  When the user specified volume is reached, the meter register will send a signal to the control system that will direct the softener to begin delayed regeneration at a user-set time.  The meter body shall be constructed of stainless steel or cast bronze.

5.3       Twin Alternating System (Metered)

The twin water softener shall be equipped with one (1) turbine or paddle-type water meter in the common outlet header.  When the user specified volume is reached, the meter register will send a 120 volt signal to an alternator stager that will direct the softener presently on-line to begin regeneration immediately while placing the stand-by softener into service mode.

System shall produce a continuous supply of soft water.

5.4       Multiple Tank Parallel Progressive (Metered)

The system shall consist of (two) or (three) resin tanks each having a dedicated turbine or paddle-type flow sensor in the softener outlet piping and operate in the parallel progressive flow configuration.

Resin tank, designated as the primary, will remain on-line at all times.  Variation of treated water flow demand shall automatically cause one additional resin tank (up to two additional resin tanks) to change status from standby to on-line and back to standby as needed.  When the primary media tank regenerates, the next resin tank in sequence shall become the primary.

As each resin tank user set volume is reached, it will immediately be taken off-line, regenerated and placed immediately back on-line or standby depending on treated water flow demand.  The controller shall be capable of continuously determining the exhaustion rate of each media tank thus automatically avoiding the possibility of a simultaneous regeneration attempt.  Simultaneous regenerations are not possible.

The exchange capacity of each softener can be the same or different.  Flow rate or peak flow rate indication shall be continuously displayed for each unit.  The continuous flow range is 0 – 999 flow units per minute (gallons, cu-ft., liters, cu-m, etc.).  Cumulative volume totalization to eight (8) digits shall be continuously displayed for each unit.

- ACCESSORIES

  - Water test kits for hardness test shall be supplied to conduct soap drop test.

  - Pressure Gauges for hard water inlet and soft water outlet.

  - Sampling Cocks for hard water inlet and soft water outlet.

7.0  INSTRUCTIONS

A complete set of installation, operating and maintenance manuals shall be provided.

- FIELD SERVICE

The services of a factory authorized service representative shall be made available to supervise, inspect and provide operator training as required for initial start-up and system operation.

- WARRANTY / GUARANTEE

Attrition loss of mineral is guaranteed not to exceed 3% per year for a period of three (3) years.

All mechanical and electrical equipment is guaranteed for one (1) year against any defects in workmanship or materials.  Any part proving defective shall be replaced or repaired within this period at manufacturer’s option.

The manufacturer guarantees that under actual operating conditions the mineral shall not be washed out of the system during the service run or backwashing period; and that the turbidity and color of the effluent, by reason of passing through the softener system, shall not be greater than the incoming water; and that the underdrain system, gravel and minerals shall not become fouled, either with turbidity or by dirt, rust or scale from the softening system while operating as noted in manufacturer’s instructions.